## Slide 1: WP05, Power Coupler Interlock XTL Installation
Main Linac Installation Meeting, April 22nd 2014
W.-D. Moeller, MHF-SL
For A. Goessel, M. Mommertz, C. Mueller, D. Tischhauser, T. Buettner, MHF-SL
T. Delfs, P. Pototzki, MCS 2
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: WP05 Components
RF Power Coupler (CPL)
IKC from LAL, Orsay, are delivered together with the Cryo-Modules
Technical Interlock (TIL) for the RF Power Coupler
Contribution from MHF-SL
  For 808 x 1.3GHz Power coupler
  For 8 x 3.9GHz Power coupler
  For one Gun RF Power Coupler
RF Power Coupler Mover (Qload tuning)
Contribution from MCS 2
  For 808 x 1.3GHz Power coupler
RF Power Coupler Bias
optional in case of MP, no development and fabrication so far
Notes: Before you start editing the slides of your talk change to the Master Slide view:
Menu button “View” > Slide Master:
Edit the following items:
1. On the Title slide (second master slide)
a) Click to add title of your talk
b) Click to add subtitle (conference, location, name of the speaker, date)
2. On the Slide Master (first master slide)
a) The 1st row in the violet header: Delete the existent text and write the title of your talk into this text field b) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area.
Close Master View

## Slide 3: Interlock signals
1 Vac/Cryo section = 3 RF groups
1 RF group = 4 modules
1 module = 8 cavities and couplers
IL signals for one cavity and coupler:
    LUWG Spark detector
    3 x e-
    T300K (PT1000)
    2 x T70K (PT1000)
Additional we have the following signals in one RF group, to generate the alarm signal for the LLRF and the klystron:
    Cryo section OK (end of a section, He-pressure & -level)
    4 x Coupler vacuum (ion getter pump (IGP) on each module)
    2 x Cavity vacuum (ion getter pump on each end of a section)

## Slide 4: The Cryo-Module
panel
Coupler interface
coupler
module feedthroughs
motor

## Slide 5: Technical Interlock, Diagram
FPGA board

## Slide 6: TIL Rear Transition Module (MTCA.4 RTM TIL)
coupler version
  For 4 couplers
    per coupler: 3 x e-, 2x Temperature, 1x spark, test functions
vacuum/ He version
    16 channel analog in (U/I 14bit)
    8 channel temperature
10 layer, 2832 elements

## Slide 7: Technical Interlock Rack Installation
Rack interfaces

## Slide 8: IL Tunnel Cable Diagram of one RF Station
Rack1, master
Rack IF
alarm IF
Module2
Module1
Klystron
Module 3, 4
Panel 2
Rack2, slave
Rack IF
alarm IF
Vacuum
Cryo OK
Panel 1
MPS
4x
4x
Coupler mover
Coupler mover

## Slide 9: List of Components and Status
component | tested | available | Series order | status
CPL interface | yes | 120, (15 cryo-modules) | all | ongoing production
TIL sensors | yes | yes | all | Production ongoing
Module cable trees, panel | yes | 20, (10 cryo-modules) | all | Production ongoing, assembly by IFJ-PAN
Rack interface | yes | 16, (1.5 rf stations) | all | Series delivery June 2014
Alarm interface | development | Prototype May 2014 | June 2014 | Series delivery Aug 2014
DAMC02 | yes | 10 (1 rf stations) | all | Production ongoing
TIL-RTM | yes | 16 (1.5 rf stations) | May 2014 | Series delivery July 2014
µTCA crate, CPU, MCH, SSD, power supply | yes | 1 RF station | all | Centralized ordering by MCS 4
Rack cable | yes | 2 RF stations | in preparation | Order after test assembly
Tunnel cable (rack to module) | Not needed | yes | In progress | Cables are ordered by MDI, design in KDS

## Slide 10: XTL Module Installation
Sensors, coupler interface and cabling on cryo-modules are assembled prior to the module test (incl. piezo, RF, cryo sensors, coupler mover)
Module test in AMTF includes (besides of cavities, tuner…)
  Sensors
  Coupler interfaces
  Cabling and connections
  Cable calibration
  Coupler mover
Module installation in XTL as a fully tested unit (WG distribution is tested and assembled separately)

## Slide 11: XTL Rack Components Installation
First RF station:
Rack installation test is in progress at MHF-SL
Final installation of the rack for the first RF unit in XTL asap
Definition of all cables at first rack installation in XTL
Series fabrication of tunnel cable for all RF units (MDI)
Where to install TIL in the racks for next RF stations will be decided after first experience:
Pre-installation of racks in XTIN or
Locally in XTL

## Slide 12: WP05 Technical Interlock Installation Manpower
Electronic development and testing
  A. Goessel
    M. Mommertz
    D. Tischhauser
Electronic-lab installation and testing
  C. Mueller
    N. Engling
    D. Mueller
    S. Oehler
    E. Schumann
    N. Deglau
RF- development
  T. Buettner

## Slide 13: WP05, TIL
Thank You