## Slide 1: XFEL Cryo Operation DESY Betriebsseminar Grömitz 25.03.2015
Tobias Schnautz-MKS1-, Kolja Stapf-MKS1-, Matthias Clausen-MKS2-
Bernd Petersen-MKS-
laufende Inbetriebnahme durch LINDEKRYOTECHNIK
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: Outline
XFEL Refrigerator – general requirements
Re-use of HERA refrigerators
Sequence of installation and commissioning
Some technical details – background of CCs
Preliminary results of comissioning
Installation & commissioning schedule
RF load/ electrical heater compensation
Some remarks
Summary
Notes: Before you start editing the slides of your talk change to the Master Slide view:
Menu button “View” > Slide Master:
Edit the following items:
1. On the Title slide (second master slide)
a) Click to add title of your talk
b) Click to add subtitle (conference, location, name of the speaker, date)
2. On the Slide Master (first master slide)
a) The 1st row in the violet header: Delete the existent text and write the title of your talk into this text field b) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area.
Close Master View

## Slide 3: Requirements on XFEL Refrigerating Plant Decision to use HERA Refrigerating Plant for XFEL
100 cryomodules, 10 Hz, Qo=10**10, 23.6 MV/m
Requirements on XFEL refrigerating plant (17.5 GeV)
1 injector, 3.9 GHz + 1.3 GHz cryomodule
2K: 1869 W
5/8K: 3593 W
40/80K: 23923 W
Operation: 24 h/d, 7 d/week
Run periods of 2-3 years without scheduled break
Refrigerator availability > 99%

## Slide 4: Requirements on XFEL Refrigerating Plant Decision to use HERA Refrigerating Plant for XFEL
  Study was conducted 2006
Industrial Study Linde Kryotechnik and its Results:
Based on TDR XFEL refrigerator requirements
Subject: re-use of HERA refrigerator for XFEL
Process investigation including CC operation (cold compressors)

## Slide 5: Requirements on XFEL Refrigerating Plant Decision to use HERA Refrigerating Plant for XFEL
5
  2 HERA refrigerators (subplants) + 2K system (cold compressors) could be modified to XFEL-refrigerator
Industrial Study Linde Kryotechnik and its Results:
Advantages:
Only ½ of investment costs compared to new refrigerator (fixed price for 2006)
No extra civil engineering effort
Utilities exist
Disadvantages:
Lower efficiency compared to new plant
Re-use of worn equipment
Parallel operation of 2 cold boxes challenging (symmetrical operation)
Use of existing HERA helium refrigerator = cheapest solution (decreasing investment costs for the XFEL refrigerator about factor 2) reason to realize this solution

## Slide 6: HERA Refrigerating Plant -> XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 42
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
HERA North
HERA South
FLASH,
CMTB,
MTH,
AMTF,…

## Slide 7: HERA Refrigerating Plant -> XFEL Refrigerating Plant Commissioning of XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Overhauling
Commissioning of both XFEL subplants
Started August 2013

## Slide 8: HERA Refrigerating Plant -> XFEL Refrigerating Plant Commissioning of XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Commissioning of both XFEL subplants together with DB54 was continued until November 2013

## Slide 9: HERA Refrigerating Plant -> XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL

## Slide 10: HERA Refrigerating Plant -> XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
Distribution Box
XLVB
Shaft
(Building 54)
Cryo Plant

## Slide 11: HERA Refrigerating Plant -> XFEL Refrigerating Plant Commissioning of XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Problem: Transferline XRTL was delayed (~1 year)
Commissioning of Cold Compressor Box (CB44)
Cold compressor box CB44 couldn‘t be commissioned ‚in time‘
Time loss is not acceptable
CB44 was temporarily installed in building 54 with ‚commissioning transferline CXRTL‘ February – September 2014 (30 weeks !)

## Slide 12: HERA Refrigerating Plant -> XFEL Refrigerating Plant Commissioning of XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
CXRTL
Cold Compressors
CB44
Distribution Box
DB54
Pre-commissioning of XFEL refrigerator with CB44 in building 54
Until September 2014
Partial compensation of delayed XRTL

## Slide 13: HERA Refrigerating Plant -> XFEL Refrigerating Plant Commissioning of XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
CXRTL
Cold Compressors
CB44
Distribution Box
DB54
Transport of CB44 from building 54 to final location of installation in XSE
December 2014
Time can be used for further tests (symmetrical operation of both subplants)

## Slide 14: Transport of CB44 to XSE

## Slide 15: HERA Refrigerating Plant -> XFEL Refrigerating Plant Commissioning of XFEL Refrigerating Plant
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
October 2014 – March 2015
Installation of transferline XRTL
March - May 2015
Final commissioning of XFEL refrigerator with CB44 in XSE

## Slide 16: Installation of XRTL Transferline completed
In cold operation since week 12

## Slide 17: Overview of XFEL Cryogenic Equipment
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Distribution Box
XLVB
Injector
Warm
He-Pumps
AMTF
Linac
XLVB installation in XSE started week12 2015

## Slide 18: 19.March 2015 – XLVB in XSE

## Slide 19: Overview of XFEL Cryogenic Equipment
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Distribution Box
XLVB
FB
CM
FC
EC
3,9 GHz
Injector
Distribution Box
XIVB
FB
CM
FC
EC
3,9 GHz
AMTF
First cool-down of injector
June 2015
Warm
He-Pumps
Linac

## Slide 20: Cryogenic injector equipment installed
Some remaining work for injector components will be completed in April

## Slide 21: Overview of XFEL Cryogenic Equipment
Warm
He-Pumps
SC
SC
SC
Colbox 43
SC
Purifier
SC
SC
SC
Colbox 41
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Distribution Box
XLVB
FB
CM
FC
EC
3,9 GHz
Injector
Distribution Box
XIVB
FB
CM
FC
EC
3,9 GHz
AMTF
Main Linac
– June 2016
June 2016 start of linac cryo operation
XLTL1
XLTL3
XLTL2
CMS
FC
EC
CMS
FC
EC
CMS
SCB
EC
CMS
FC
SCB
Linac

## Slide 22: Installation of cryogenic equipment (shaft) Sequence (shaft)
Cold Compressor Box
CB44
Distribution Box
XLVB
Transferline to XFEL refrig. plant
XRTL
Transferline to linac
XLTL1 (vertical)
Transferline to linac
XLTL1 (horizontal)

## Slide 23: Modification of the Coldboxes The effect from 4.5K to 2K
To be modified
To be removed
No changes
LN2 heat exchanger removed
Re-arrangement of turbine strings
50% of piping modified

## Slide 24: Modifications of the refrigerator Coldboxes The effect from 4.5K to 2K…
Modifications
50% of all piping were modified
LN2 precooling heatexchanger was removed
Turbines were re-arranged and equipped with optimised flow parts
At least some items remained
Platefin heatexchangers
80K and 20K Adsorber
Cryogenic valves (shaft, stem and some plugs)
17 years of operational experience  atuomated procedures migrated into plc

## Slide 25: Overhaul of the Compressor System Facts & figures
Main Objective
To ensure «a sufficient helium-supply of the XFEL-linac for at least 15 years of continuous operation» [from T. Schnautz, B. Petersen «Specification of the XFEL-Refrigerator»]
Some numbers about overhauling:
Adsobent replacement at 4 dryers
Revision of 9 screw compressor blocks
Calibration of 178 safety valves
New sealings at 1292 manual valves
Painting of all equipment overhauled
Pressure & leak test

## Slide 26: New Components: 2K Cold Compressors (1)
Some facts about cold compressors
Small dynamic range
Sensitive towards massflow-, pressure-, temperature changes
Each system is unique
(Re-)start of cold compressors is time intensive
DESY has no operational experience with cold compressors

## Slide 27: Cold Compressors (2) Cold Compressor Bypass Operation
x %
x %
(100-x) %
2K Return
2K Return
Cold Compressor Box CB44
4 cold compressors, total compression ratio = 45.8
Full flow re-cooling bypass
Startup & pumpdown independent from «experiment side»
Operational robustness due to high internal turndown ratio
CC kept in operating map

## Slide 28: Screen Shot from CSS Applications SDS (Synoptic Display Studio)

## Slide 29: Screen Shot from CSS Applications SDS Correlation Plot

## Slide 30: XFEL Refrigerator Capacity Spec
Start-up: 17.5 GeV version
Design Spec:
2K: 1896 W
5K: 3593 W
40K: 23923 W
DESY specification for XFEL refrigerating plant
Operating 17.5 GeV Linac with one refrigerator (subplant) would save > 500.000 EUR primary energy costs
LINDE ‚TS‘ prognosis:
( for one coldbox):
2K: 2010 W
5K: 3030 W
40K: 20175 W
Parallel Operation of 2 Cold Boxes to achieve specified design capacities
Hope: operation of only one cold box for XFEL linac supply

## Slide 31: Commissioning of XFEL Refrigerating Plant
Distribution Box
XLVB
Distribution Box
XLVB
Comissioning of screw compressors, sub-systems, cold-boxes an DB54 until November 2013 (NO demonstration of CB capacities !)
Comissioning of CB44 (CCs) and capacity measurements February-September 2014
- start of CCs operation fast, smoothly & promising, bypass works !
- demonstration of capacities failed, low performance of CBs
‚Root-Cause-Analysis‘ to fix low performance of CBs
December 2014 – January 2015 repeated capacity tests of CBs
(CB44 separated, modified ‚test-caps‘)
Since March 2015 – complete comissioning including XRTL and CB44 in final position

## Slide 32: LINDEKRYOTECHNIK Root Cause Analysis

## Slide 33: Modified Testprocedures for Commissioning

## Slide 34: Capacities of Cold-Boxes (preliminary)
CB41
CB43
(2) Comment: 2K capacity of 13 KW ist the heater equivalent of 100 g/s in TS-diagram

## Slide 35: Final Comissioning – CB44 in XSE
Verification of cooling capacities including CCs operation
(for single cold box operation)
Demonstration of parallel cold box operation
(verification of specified design capacities)
Demonstration of part load operation of CCs
(JT screw compressor in sub-atmospheric operation)

## Slide 36: Final Comissioning & Installation Schedule
XFEL refigerator comissioning until mid May
Until mid May: installation of XLVB (BINP)
Until mid May: complete injector installation (BINP)
May-June installation of final transfer CB44-XLVB
Until mid may: complete warm gas tubing
July: start of injector cryo operation
XLVB not yet connected to linac ! Endcap at XLVB
4 weeks break of injector operation for final connection to XFEL linac in 2016
XFEL helium purifier ordered

## Slide 37
37
MKS Internal Presentation
Dr. S. Putselyk, DESY
RF load / electrical heater load compensation
Experiments are going on in FLASH, CMTB, AMTF
J.Branlard –MSK-,S.Putselyk –MKS1-, M.Clausen –MKS2-

## Slide 38
Some Remarks
Repair / replacement of cooling water supply required -MKK-
(old HERA cooling towers leaky)
Energy recovering system will be added to HD screws –D5,MKK

## Slide 39: Summary
Installation of XFEL refrigerator completed
First operation of cold compressors demonstrated
Cooling capacity of single cold boxes verified
Single cold box operation for XFEL linac supply seems to be possible
To be demonstrated: final capacities incl. CCs operation
To be demonstrated: part load operation of CCs
To be demonstrated: parallel cold box operation
On schedule for supply of injector and linac

## Slide 40
Vielen Dank fürs Zuhören !