## Slide 1: WP05, Coupler Technical Interlock (TIL)
Patch panel on modules are missing or relocated
Cabling rack - modules:
  Cables for patch panel to rack are missing
  Cables for coupler mover to rack are missing
  Cables for vac. and cryo. signal to rack are missing
  Grounding is missing
Rack:
  collision of TIL access space with IT cables
  AC installation still open
Conditioning software to be done (peak power measurement for reliable measurement is missing)
Schedule: better understanding after 03/15
3.11.14, W.-D. Moeller, MHF-SL