## Slide 1: High Voltage Power Module
pluggable to NAT RTM Power Supply Carrier
Konrad Przygoda
Michael Fenner,
DESY
Helmut Lauftkoetter,
NAT

## Slide 2: Outline
Motivation
Hardware
Firmware
Software
Results
Possible applications

## Slide 3: Motivation
DESY introduced an RF-Backplane for MicroTCA.4 Crates
  The RF-Backplane is located behind the AMC backplane of the MicroTCA.4 Crate.
  Three types of RTMs used: µRTMs with only a Zone-3 connection to the front AMCs, µRTMs with a connector to the RF-Backplane and optionally a Zone-3 connection to the front AMCs and extended RTMs
eRTMs are not covered by MicroTCA.4 Specification, a standard Power Modules does not provide power to them
µRTMs used together with the RF-Backplane might be powered from the RF-Backplane instead of corresponding to a given AMC board
In many cased sensitive analog signal conditioning elements are installed on RTMs and there is a need to provide clean power supply to these RTMs
For specific applications there is a need to deliver high voltage, high current power supply which is not covered by MicroTCA.4 Specification

## Slide 4: Hardware (RF-Backplane)
Rear PM
Rear PM
Courtesy by H. Lauftkoetter

## Slide 5: Hardware (Example Setup)
+/-100V
Courtesy by H. Lauftkoetter

## Slide 6: Hardware (NAT RTM Power Supply Carrier)
High quality ±VV for µRTMs, adjustable 5-12V
+12V PP, +3.3V MP for eRTMs
Contention protection against standard PMs
Modular design
Optional ±100V output at front panel
AC frontend
Courtesy by H. Lauftkoetter

## Slide 7: Hardware (High Voltage Power Module)
Accept low voltage input (up to +48 VDC) and deliver stable, high voltage (up to ±100 VDC – bipolar or unipolar) and high current (up to 500 mA) outputs
PMBus standard communication bus
Temperature, output voltage, current and power sensors
Allow supplying up to 4x RTM cards
High voltage output indicated by front panel LEDs
Built in: short circuit protection, input filter
Inputs/outputs isolated with possible line, load regulation
Closed inside housing (Nickel Plated Copper),
Cooled using free air convection (no additional heat sink needed)

## Slide 8: Firmware (ATXMEGA128A1U)
hvpm.c
  void HVPM_DriverInit(); void HVPM_ActivateHVPos(); void HVPM_DeactivateHVPos();
  void HVPM_ActivateHVNeg(); void HVPM_DeActivateHVNeg();
  void HVPM_ActivateHVPosNeg(); void HVPM_DeActivateHVPosNeg();
  void HVPM_TemperatureSenseHVPos(); void HVPM_TemperatureSenseHVNeg();
  void HVPM_VoltageSenseHVPos(); void HVPM_CurrentSenseHVPos();
  void HVPM_PowerSenseHVPos(); void HVPM_VoltageSenseHVNeg();
  void HVPM_CurrentSenseHVNeg(); void HVPM_PowerSenseHVNeg();
hvpm.h
  #define MAX6626A_ADDR (0x48)
  #define MAX6626B_ADDR (0x49)
  #define LTC2945A_ADDR (0xD8>>1)
  #define LTC2945B_ADDR (0xDE>>1)
  …

## Slide 9: Software
NAT RTM PSC menu
HVPM submenu

## Slide 10: Results

## Slide 11: Possible Applications (XFEL RF Station – 32 cavities)
DRTM-VM2
DAMC-TCK7
AMC-SIS8300
RTM-DWC10
FPGA
FPGA
AMC-SIS8300
RTM-DWC10
FPGA
8x RF in
(probe)
1x KLY
8x RF in
(forward)
AMC-SIS8300
RTM-DWC10
FPGA
8x RF in
(reflected)
Cavity tuner control – pulse or cw modes
1x
2x
DRTM-PZT4
DAMC-FMC25/20/TCK7
FPGA
PZD
4x Vpiezo
8x
DAMC-FMC25/20/TCK7
FPGA
SFP
32x cavities = 64x piezos
2x
2x
2x
2x
2x
2x
2x
8x
1x
2x12
Slot
Crate
1x12
Slot
Crate

## Slide 12: Possible Applications (XFEL link stabilization)
DAMC-FMC25
DAMC-FMC25
RTM-AD84
FPGA
FPGA
4x OXC
6x
DRTM-PZT4
DAMC-FMC25/20/TCK7
FPGA
PZD
4x Vpiezo
6x
DAMC-FMC25/20/TCK7
FPGA
SFP
24x links = 24x piezo fiber stretchers
2x
1x
6x
6x
1x
1x12
Slot
Crate
1x12
Slot
Crate
RF Master Oscillator
Master Laser Oscillator
RF
Links
REFM
REFM
REFM
3x
REFM
REFM
REFM
REFM
REFM
SEED
SEED
PPL
INJL
BAM
2x
BAM
2x
BAM
2x
BAM
BAM
Links
Master Laser Oscillator
Links
Synch Hutch
10-12 Links
12 RF Links
Sub-Synch Hutch
? Links
? RF Links
1-6x
3x
2x
2x
2x
2x
2x
INJL
REFM
REFM
BAM
Link Stabilization
Courtesy by C. Sydlo

## Slide 13: Possible Applications (XFEL Master Laser Oscillator Sync)
DAMC-FMC25
DAMC-SIS8300
RTM-DWC10
FPGA
FPGA
2x RF in
2x
1x
2x
1x12
Slot
Crate
Courtesy by U. Mavric
Laser Synchronization
DRTM-PZT4
PZD
1x Vpiezo
2x
1x
Redundant
solution
Before connecting your AMCs with serial links over the AMC backplane study its show_fruinfo 253

## Slide 14: Possible Applications (many more)
bERLinPro at HZB
TARLA in Ankara
ESS?
Courtesy by P. Echeverria

## Slide 15: Thank You for Attention