## Slide 1: PETRA III Operation 2018
Michael Bieler
Travemünde, Febr. 21, 2019

## Slide 2: Agenda
01 Operation 2018
02 Availability
03 Conclusion

## Slide 3: Operation 2018

## Slide 4: Operation 2018
Schedule
External users from March 26 to July 17
and from Sept. 3 to Dec. 20

## Slide 5: Operation 2018
Summer Shutdown 2018
Straight section north, damping wigglers:
Hole in the wall for P61
Exchange of last absorber in damping wiggler section
Installation of front end for P61 in the tunnel, including a power absorber
First light in the front end of P61
15.8.2018

## Slide 6: Operation 2018
Summer Shutdown 2018
Straight section East:
Removal of the temporary In-Vacuum-Undulator PU21b
Installation and bake out of the final In-Vacuum-Undulator PU21b
PU21b, IVU
27.08.2018:
First monochromatic light from the IVU, PU21b
5.9.2018:
First proof of principle diffraction pattern from the IVU, PU21b

## Slide 7: Operation 2018
PU21a
PU21b, IVU
17.9.2018:
First proof of principle diffraction pattern from the ‘baby undulator’ PU21a

## Slide 8: Operation 2018
PU21b, IVU
PU04
Sept. 10 2018: First light at the end of the new branch of P04

## Slide 9: Operation 2018
PU21b, IVU
Timing Mode
Timing Mode:
40 Bunch operation with 100 mA beam current became unstable. Spontaneous beam losses of 10-15 mA happened ~ daily.
Cure:
40 bunch mode with 90 mA beam current, no instabilities.
Experiments prefer stable operation.

## Slide 10: Operation 2018
PU21b, IVU
PU22
At the same time P07 requested a low beta optics. This was established, for the first time with PU21 in the straight section east. Less degrees of freedom for tuning the optics, low beam life time, high emittance.
This optics needs more attention.
The very first beam time at beamline P22 was very successful.
Therefore P22 requested a change in schedule:
Another 10 days of timing mode.
As a compromise a ‘mild’ timing mode with 80 bunches was delivered in October.
Again very successful experiments at P22.
80 bunches,
low beta

## Slide 11: Operation 2018
PU21b, IVU
Winter Shutdown 2018/2019
In the arc West Right:
Installation of 10 NEG coated dipole chambers, NO bake out (Test for PETRA IV)
Max von Laue Hall:
Removal of the temporary 2 m undulator PU7 (after 8 years)
Installation and bake out of the final In-Vacuum-Undulator PU7 (former temporary PU21b)

## Slide 12: Operation 2018
PU21b, IVU
Plans für 2019
External users from March 11 to July 14
and from Aug. 5 to Dec. 19

## Slide 13: Operation 2018
PU21b, IVU
Statistics
5 bunch patterns:
Timing Mode
  40 bunches, 192 ns
  80 bunches, 96 ns
Continous Mode
  240 bunches, 32 ns
  480 bunches, 16 ns
  960 bunches, 8 ns
User Run 2018
Scheduled time: 4231 h
55 % Timing Mode (40/80 Bunches)
Availability 96,4 %
Chart: 
| TIMING 40 | TIMING 60 | CONT 240 | CONT 480 | CONT 960
 | 0.50659 | 0.045371 | 0.034029 | 0.41401 | 0
80

## Slide 14: Availability

## Slide 15: Availability
PU21b, IVU
Chart: PETRA III Availability 2018
| 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51
AV_W | 74.7445 | 99.1551 | 96.4352 | 99.456 | 25.9524 | 99.7516 | 81.6319 | 99.5949 | 99.0162 | 99.6412 | 93.5614 | 92.9437 | 99.8148 | 99.8032 | 85.5903 | 97.7778 | 93.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4504 | 92.9745 | 98.1829 | 99.8264 | 100 | 100 | 96.8613 | 98.9699 | 98.3532 | 99.5833 | 100 | 99.2092 | 100 | 98.6921 | 97.6736 | 100
TARGET | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
AV_Y | 74.7445 | 87.2539 | 90.3647 | 92.6655 | 91.8547 | 93.5798 | 91.6269 | 92.7463 | 93.5187 | 94.1901 | 94.1477 | 94.0348 | 94.5251 | 94.9377 | 94.2599 | 94.4977 | 94.4669 | 94.4669 | 94.4669 | 94.4669 | 94.4669 | 94.4669 | 94.4669 | 94.6799 | 94.5816 | 94.778 | 95.039 | 95.3213 | 95.3323 | 95.4 | 95.5586 | 95.6963 | 95.8539 | 95.862 | 95.9861 | 96.1366 | 96.2289 | 96.2793 | 96.3699
weekly average
goal
yearly average
96.4 %
Studies,
Testruns
2017:
98 %

## Slide 16: Availability
PU21b, IVU
MTBF
Definition:
Mean Time between Failures =
number of faults
delivered beam time
50:00 h
Studies,
Testruns
2017:
42:37 h

## Slide 17: Availability
PU21b, IVU
Comparison
PETRA III
6 GeV
2304 m
1.4 nm
96.4 % (2019)
50 h

## Slide 18: Availability
PU21b, IVU
Faults statistics
Chart: 
| RF | PS | WK | IL | VAC | INST | SAFETY | OP | LINAC | UNKNOWN | SEKI | POWER_GLITCH | DESY | FEEDBACK | TIMING | PIA | LONG_INST | INTL | EXP | SCHEDULED
SUM FAULTS | 13 | 16 | 0 | 0 | 3 | 2 | 1 | 1 | 3 | 5 | 0 | 9 | 2 | 5 | 5 | 1 | 0 | 2 | 10 | 1
Chart: 
| RF | PS | WK | IL | VAC | INST | SAFETY | OP | LINAC | UNKNOWN | SEKI | POWER_GLITCH | DESY | FEEDBACK | TIMING | PIA | LONG_INST | INTL | EXP | SCHEDULED
SUM FAILURE TIME | 0.25556 | 1.009 | 0 | 0 | 0.12778 | 1.4368 | 0.017361 | 0.20694 | 0.28194 | 0.10625 | 0 | 1.0097 | 0.21875 | 0.27292 | 0.86458 | 0.084028 | 0 | 0.21597 | 0.275 | 0.018056

## Slide 19: Availability
PU21b, IVU
Faults statistics
Failure time:
Dominated by 3 disasters (red bars).
Together they represent
64 h failure time
42 % of the total failure time
1.5 % availability
Chart: 
| RF | PS | WK | IL | VAC | INST | SAFETY | OP | LINAC | UNKNOWN | SEKI | POWER_GLITCH | DESY | FEEDBACK | TIMING | PIA | LONG_INST | INTL | EXP | SCHEDULED
SUM FAILURE TIME | 0.25556 | 1.009 | 0 | 0 | 0.12778 | 1.4368 | 0.017361 | 0.20694 | 0.28194 | 0.10625 | 0 | 1.0097 | 0.21875 | 0.27292 | 0.86458 | 0.084028 | 0 | 0.21597 | 0.275 | 0.018056

## Slide 20: Availability
PU21b, IVU
Faults statistics
Instrumentation, 28.3.2018:
Vacuum leak at a beam current monitor. 30 minutes after a beam dump the pressure went up. 200 m storage ring and 4 frontends vented.
31 h lost.
Monitor build in 2008, no longer used, temperature no longer monitored.
Thorough investigation:
Vendor consulted
Broken surface inspected in material science lab
Temper colors normal
RF field calculations: 46 W deposited (currently used design: 16 W)
No reason found.
Lesson learned:
Remove all unnecessary components to reduce risks.

## Slide 21: Availability
PU21b, IVU
Faults statistics
Timing, 5.7.-7.7.2018:
Timing jumps lead to longitudinal instabilities and beam losses.
Reason unknown, components exchanged ‘randomly’. Very few experts working day and night.
Finally found: A faulty 500 MHz synthesizer in the timing system did phase jumps in the µs range.
20:45 h lost.
Lessons learned:
Timing had
not enough diagnostics (added here)
not enough experts.
Timing jumps

## Slide 22: Availability
PU21b, IVU
Faults statistics
20:45 h lost.
phase jumps in the µs range.

## Slide 23: Availability
PU21b, IVU
Faults statistics
12 h lost.
Power Glitch, 9.5.2018, 11 PM:
Flash in a 10 kV switch on site.
DESY lost 2 of 3 power feeds.
PETRA III and FLASH affected. Buildings are dark, many broken components.
10 kV back after 2 hours.
On call services on site all night (after a full working day).
10.5.2018 is Ascension Day, national holiday, no fresh personal available. Several volunteers come in.
PETRA III user operation is supposed to start 10.5. 7 AM.
No beam before 10.5. 7 PM.
The 10 kV switch was investigated by
DESY personal
experts from the local power provider
The switch had been serviced regularly.
No reason for the fault found. The switch is back in operation.
Lesson learned:
A power outage on the night before a public holiday is hard to cover.
Service Day
Test Run
User Run
Power
Outage

## Slide 24: Availability
PU21b, IVU
Faults statistics
Chart: 
| RF | PS | WK | IL | VAC | INST | SAFETY | OP | LINAC | UNKNOWN | SEKI | POWER_GLITCH | DESY | FEEDBACK | TIMING | PIA | LONG_INST | INTL | EXP | SCHEDULED
SUM FAILURE TIME | 0.25556 | 1.009 | 0 | 0 | 0.12778 | 1.4368 | 0.017361 | 0.20694 | 0.28194 | 0.10625 | 0 | 1.0097 | 0.21875 | 0.27292 | 0.86458 | 0.084028 | 0 | 0.21597 | 0.275 | 0.018056
Failure time (w/o the 3 major events):
Magnet power supplies: Long time to repair.
Power glitch: Mainly from outside DESY.
The rest is equally distributed

## Slide 25: Availability
PU21b, IVU
Faults statistics
Chart: 
| RF | PS | WK | IL | VAC | INST | SAFETY | OP | LINAC | UNKNOWN | SEKI | POWER_GLITCH | DESY | FEEDBACK | TIMING | PIA | LONG_INST | INTL | EXP | SCHEDULED
SUM FAULTS | 13 | 16 | 0 | 0 | 3 | 2 | 1 | 1 | 3 | 5 | 0 | 9 | 2 | 5 | 5 | 1 | 0 | 2 | 10 | 1
Number of faults:
RF: High, but improved. No venting, no tests.
Magnet power supplies: High number of components.
Power glitch: Mainly from outside DESY.
Experiments:
  Users opening doors,
  Front End electronics,
  Undulator faults

## Slide 26: Availability
PU21b, IVU
Faults statistics
Number of faults per 1000 h:
Mainly consistent with previous years.
Chart: 
| RF | PS | WK | IL | VAC | INST | SAFETY | OP | LINAC | UNKNOWN | SEKI | POWER_GLITCH | DESY | FEEDBACK | TIMING | PIA | LONG_INST | INTL | EXP
2013/14 | 11.3548 | 3.2688 | 0.34409 | 0 | 0.68817 | 0.68817 | 0.17204 | 1.3763 | 0.86022 | 1.2043 | 0.34409 | 1.0323 | 1.3763 | 0.17204 | 0.68817 | 0.17204 | 0.17204 | 0.86022 | 2.0645
2015 | 6.5522 | 2.883 | 3.1451 | 0 | 0.26209 | 0.52418 | 0 | 3.1451 | 1.5725 | 3.9313 | 1.8346 | 2.6209 | 0.26209 | 0.78627 | 0.26209 | 0.26209 | 1.3104 | 0 | 0.78627
2016 | 8.3691 | 4.0715 | 0.45239 | 0 | 0.67858 | 0.22619 | 0.22619 | 0.67858 | 0.22619 | 1.131 | 0.45239 | 1.5834 | 2.2619 | 1.131 | 0 | 0 | 0 | 0.45239 | 2.0357
2017 | 5.4993 | 4.2495 | 0.24997 | 0 | 0.74991 | 0 | 0.24997 | 1.7498 | 0.99988 | 0.99988 | 0.49994 | 1.2498 | 0.74991 | 0.99988 | 0.99988 | 0.24997 | 0 | 0.24997 | 2.4997
2018 | 2.8626 | 3.8168 | 0 | 0 | 0.31807 | 0.63613 | 0.31807 | 1.2723 | 0.63613 | 2.2265 | 0 | 2.5445 | 0.31807 | 0.9542 | 1.5903 | 0 | 0 | 0.63613 | 2.2265

## Slide 27: Conclusion

## Slide 28: Conclusion
PU21b, IVU
Availability 2018 was lower than in previous years.
3 major events dominated the statistics.
The number of faults per 1000 h is slightly improving over the years.
The MTBF is slightly improving over the years.
Both availability and MTBF are not yet in line with other facilities.

## Slide 29: Thank you

## Slide 30
Michael Bieler
-MBB-
bieler@desy.de
Tel. (9)3805