## Slide 2: Compute/Storage at CERN What lessons for Cuba?
Humboldt Highway II - computer cluster on renewable energies Tony Cass, 2nd August 2023

## Slide 3: CERN clusters are big!

## Slide 4: Compute and Config

## Slide 5: CPU type in LxBatch
Chart: 
| AMD EPYC 7302 16-Core Processor | AMD EPYC 7313 16-Core Processor | Intel(R) Xeon(R) Silver 4216 CPU @ 2.10GHz | Intel(R) Xeon(R) CPU E5-2650 v4 @ 2.20GHz | Intel(R) Xeon(R) CPU E5-2630 v4 @ 2.20GHz | Intel(R) Xeon(R) Gold 6130 CPU @ 2.10GHz | Misc Intel
# of Machines | 1652 | 2 | 967 | 737 | 252 | 70 | 11

## Slide 7: But…
… is any of this useful if you are planning a solar powered cluster?

## Slide 8: Energy Efficient Procurement
Our tenders require
  80 PLUS Platinum certified PSU
  efficient power supplies with a power factor >= 0.9 for a fully loaded system
  power consumption < 0.8W per HEPSPEC06
and
  adjudication is on a “4-year TCO price”, so expensive power-efficient servers can beat cheap power-hungry ones.
Recently purchased systems are at ~0.32-0.37W/HS06

## Slide 9: Intel/AMD or ARM?
https://indico.cern.ch/event/1106990/contributions/4991256/
https://indico.jlab.org/event/459/contributions/11823/

## Slide 10: Multi-tasking storage servers
https://indico.cern.ch/event/730908/contributions/3153390/attachments/1731269/2798159/beer_k8s_bcn.pdf

## Slide 11: Where does that power go?
HEAT!
And cooling uses still more power:
This for a 1970s building. 1.1 or better is the target for data centres today.

## Slide 12: Do you need cooling?
Parameters for CERN’s new data centre
  Inlet air temperature: 25°C
  T: 12 °C
So, can you throttle CPU power to reduce T if ambient air temperature is above 25°C?
  And will servers survive if the outlet temperature exceeds 37°C?
Remember: keep inlet air and outlet air apart!

## Slide 13: Summary
Consider power consumption when selecting equipment.
  ARM seems the right way to go…
    … but benchmark your workloads
Keep machines busy!
  An idle machine is wasting precious power!
Consider (not) cooling.