## Slide 1: Personnel Interlock Systems
B. Racky, WP-38
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: Overview
The personnel interlock system is an active safety systems for the protection of persons at
  beam operation (accelerator and experiments)
  cavity operation (dark current)
  magnet current operation
Subsystems: area search procedures, warning systems (acoustics, optics), procedures for controlled access, tunnel emergency off system…
High safety level signal paths in hardwired 60 V technology; reaction time ~ms
Connection to controls (accelerator, experiments): TINE interface; GUI
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 3: Accelerator interlock areas
XTIN2
XTIN1
XSIN
XSE
XS1
XS2
XS4
XSDU1
XS3
XSDU2
XHM
XHEXP1
XTL
XTD1
XTD6
XTD5
XTD7
XTD3
XTD8
XTD2
XTD9
XTD4
XTD10
50m
1050m
1050m
480m
361m
300m
594m
660m
267m
141m
200m
544m
220m
1
1
L
1
1
1
L
L
L
L
L
L
1
1
1
L
L
L
L
1
1
1
L
1
Media shafts or labyrinths
1: first door to set at search
L: last door to set at search
door can be opened if both neighbouring areas are searched
22 interlock areas
42 interlock doors
5 interlocked lifts

## Slide 4: Beam operation modes
Nr. | Beam in interlocked tunnels | Beam dump
1 | XTIN1 | dump1 XSE
2 | XTIN2 | dump2 XSE
3 | XTL (RF operation cold modules) | commissioning dump XS1
4 | XTIN1 or 2, XTL | commissioning dump XS1
5 | XTIN1/2, XTL, XTD1-3-5-7 XTIN1/2, XTL, XTD1-3-5-7, XTD6 XTIN1/2, XTL, XTD1-3-5-7, XTD8 (+ XTD6) | main dump XSDU1
6 | XTIN1/2, XTL, XTD2-4-10 XTIN1/2, XTL, XTD2-4-10, XTD9 | main dump XSDU2
7 | Combinations of 5 and 6 | XSDU1 / 2
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 5: Beam operation modes
8 beam warning sections
If the beam operation permission of the PI is cancelled, the klystron modulatores are switched off
  5 beam dumps
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 6: Access during partial beam operation
Required safety components in the personnel interlock:
  Beamshutters and protecting absorbers
    Beam shutters serve as shielding against bremsstrahlung but may not be hit by the beam
    The absorbers protect the beamshutters, in case of steering the beam on an absorber a damage of the vacuum system might occur
  Some bending magnets
  Permanent dipole magnets
    passive safety equipment in photon beamlines
    Movable PD in TD2 beamline interlocked
Special safety precautions for controlled access procedures to searched areas have to be foreseen!

## Slide 7: Interlocked accelerator safety components
Beamshutters, Absorbers (BS, ABS)
Magnets
Movable permanent magnet
XSIN
XSE
XS1
XS2
XS4
XSDU1
XS3
XSDU2
XHM
XHEXP1
XTIN2
XTIN1
XTL
XTD1
XTD6
XTD5
XTD7
XTD3
XTD8
XTD2
XTD9
XTD4
XTD10
Magnets to dump2 XSE
BS & ABS I2
Magnets to dump1 XSE
BS & ABS I1
Magnet combination to
dump XS1, XTD1, XTD2, (XTD20)
( DTLD, DTD1, MTD1, MDT2 (..))
BS & ABS TD2
PTD2 (movable permanent magnet for TD2 beamline )
BS & ABS TD1
BS & ABS TD6
Magnets to XSDU1 (XTD3)
BS & ABS TD9
Magnets to XSDU2 (XTD4)
BS & ABS TD8
Magnets to XSDU1 (XTD5)
Magnets to XSDU1
Magnets to XSDU2

## Slide 8: Magnets in beam distribution XS1
8
[KTLD]
DTLD
Dump XS1
[KTD1]
DTD1
MTD1
MTD2
XTL
XTD2
XTD1
[MTLD]
Access to | Beam in | DTLD | DTD1 | MTD1 | MTD2 | PTD2
XTD1 | TLD, T2 |  | off | off |  | 
XTD2 | TLD, T1 |  | on! |  | off | in
XTD1, 2 | TLD | on! | off | off | off | in
Safe magnet status for access:
PTD2

## Slide 9: Signal exchange PI / accelerator components
PI deliveres (and cancels) operation permission signals for
  klystron modulators XTIN, XTL
    Gun, Cold structure,TDS
  steering beamshutters/absorbers
    I1,I2, TD1,TD2, TD6, TD8, TD9
  TD1/2 distribution magnets
    DTD1, DTD2, MTD2
  Motion of permanent magnet PTD2
  Power supplies of all magnets (Magnetstromfreigabe)
Safety signals as input for the PI
  Positions of beamshutters and absorbers
  Bending magnets
    to the 5 dumps on
    to XTD3, XTD5, XTD4 on
  Distribution magnets
    DTLD,DTD1on; DTD1,MTD1,MTD2 off
  Permanent magnet PTD2 in TD2 beamline
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 10: Magnet current operation modes
operation clearance for magnet power supplies
5 operational sections defined
controlled access for experts during operation

## Slide 11: Interfaces with machine/equipment protection system?
Interface personnel interlock / klystron interlocks
  Soft shutdown by klystron interlock (µs) before hard shutdown by personnel interlock (ms) occurs
Steering of beamshutters by personnel interlock; input for EPS foreseen to close beamshutters if needed
?
Tasks not provided by the personnel interlock
  Survey of the beam power hitting the dumps
  Avoid missteering of the beam
  ?

## Slide 12: The End
Thank you for your attention

## Slide 13: Doors for controlled access
12 accelerator interlock doors are equipped for Controlled Access (camera, intercom,…)
CA
CA
CA
CA
CA
CA
CA
CA
CA
CA
CA
CA
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 14: Controlled Access
Problem: Controlled access to searched accelerator interlock areas during beam operation other sections
Standard safety equipment for entering a searched interlock area: interlock keys (1 per person entering)
Usually all interlock keys of a DESY- accelerator stop any beam operation of the accelerator
Danger of entering an area with the wrong key!
Solution:
  Measure1 (technical): matching locks near the interlock doors to enable the access procedure
  Measure2 (organisational): only 1 person may enter per access procedure (observed by control room staff)
  Measure3 (technical): if any access key is missing no new beam warning is possible in the entire accelerator complex

## Slide 15: Interlock areas at XS1

## Slide 16: List of RF stations
No. | purpose | structure | position of modulator | operation modes at open tunnel | responsible
1 | gun mod. | warm | XHM | absorber | WP1/ MHFp
1 | sc module | cold | XHM | abs. /warm module | WP1/ MHFp
1 | ACC3H1 | cold | XTIN UG03 | (absorber) | WP /MIN
1 | TDS | warm | XSE UG05 | - | WP /MSK
XTIN1 (same for XTIN2)
No. | purpose | structure | position of modulator | operation modes at open tunnel | responsible
25 | sc modules | cold | XHM | abs. /warm module | WP1/ MHFp
2 | TDS | warm | XSE UG05 | - | WP / MSK
XTL

## Slide 17: HF-Interlock; Geometrie im XTL
HV Modulator 1
Preamp. / RF filter
Klystron 1
Module 1
(8 cavities)
Module 2
(8 cavities)
Module 3
(8 cavities)
Module 4
(8 cavities)
Absorber 1
Absorber 2
XHM
XTL, XTIN
Personnel interlock
systems klystrons
Shortcut plates with contacts for the personnel interlock (2 contacts on each plate)
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 18: Klystron operation modes
Operation modes
  (1) tunnel open
  RF absorbers
  (2) tunnel open
  RF warm modules
  (3) tunnel closed
  RF cold modules
>=1
Contacts short cut plate 1
Contacts short cut plate 2
Cryo: sc modules warm
LLRF: RF filter inserted
Key mode: linac warm
XTL / XTIN beam permission
Emergency off
Feedback „modulator Off“
&
&
&
Klystron interlocks
HV klystron modulator