## Slide 1: Rack space, power, water and air-conditioning estimates for SPB expt. hutches
This update: 12.4.2012
Input: A.Mancuso, A.Aquila, N.Coppola, C.Youngman+…
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: SPB Beamline

## Slide 3: Results (1/2)
Method:
  WP84 estimate: motors, pumps, detectors numbers
  WP76 estimate: WP84 + rest of Beckhoff + DAQ + det.cooling
Compared numbers and good agreement found
Electrical power breakdown
  98kW = motors - 5kW, pumps - 19.5kW, rest of Beckhoff - 11kW, DAQ - 32kW, DAQ extension - 30kW
  ≤ 10kW missing (fume cupboard, lights, power bars, webcams, displays)
Need 110kW of electrical power
Water cooling 80% of power in 98kW
Need 80kW of water cooling power
Expt. Hutch air-conditioning 13.5kW heat load x 2.5
Need 30kW of air-conditioning

## Slide 4: Results (2/2)
Rack space needed
What | SPB | SFX | Tunnel | Optics
Beckhoff | 2 | 1 | 0,3 | 0,1
Cooling | 1 | 4 | - | -
E-racks | 5 | 4 | 0,3 | 0,3
How to proceed suggestion:
  TC check through input spreadsheets
  TC decide on safety factors