## Questions
Responses to qurstions in red are considered important for completing the committee report
Brian Chase | Redundancy will be handled by forward and reflected power
Crosstalk between channels of 50dB will exceed phase requirements
Clock jitter of 5 ps will only allow a 55dB SNR at 54MHz IF
Injector system is currently developed in VME
Installation will be done during shutdown which is a single small window
Will there be time to install system in FLASH?
Hardware-
Describe the digital data flow on the boards and within the crate
Describe the system as a control system diagram, transfer functions, noise analysis, linearity
Why are the advantages to the baseband vector modulator as opposed to a LO- IF modulator
Hot swap, why is it needed? Is this worth the effort
How are NCOs synchronized between AMC modules?
What type of splitters will be used and what is the temperature stability of the cable plant?
Is there a Manpower assignment list?
Software-
Are there any real time requirements for the crate CPU? Answer – Linux will meet requirements.
How can Rocket IO meet the 100ns when you move data from 8 ADCs?
What is the optimum delay for noise and stability?
Why do AMC cards need to talk DOOCs?
Is the 8/9 pi mode still the stability limit?
Why do the DOOCs server integration 6m?
If the system model for the controller is linear, how is the model better than a comb filter?
Will all controllers work on a common IF frequency?
There is a lot of parallel development of complicated digital boards going on. Please comment on how this might be addressed.
Please advise us on how to address the committee chair on how to constructively address management issues in the report.
Kay Rehlich | 1) can one distribute clock (5ps RMS) and MO (.5ps) over the backplane of ATCA?
2) how big is the crosstalk for analog signals from RTM to the ADC?
3) a first prototype of an ATCA based LLRF system will be ready mid 2008. Their is no shut-down of FLASH after May. Is a test in the module test stand sufficient to demonstrate the performance?
4) if the RTM based connection scheme does not work with the required performance: what is the backup solution that allows to reuse most of the developments?
Markus Huening | 1) Is the high density (three carriers only for one RF stations) really necessary? Besides concentrating everything for one type of channel on a single carrier I see no big benefit.
On the other hand half of the crate would remain emty (or did I get that wrong?)
2) Is an separate RF crate an option? This could come with rear connectors as well but with active parts up front.
3) Is there any synergy at all between the LLRF ATCA and the general ATCA crates for the other technical groups and experiments?
Thomas Schilcher | * What is the available manpower to do the developments on ATCA platforms?
* Lots of manpower will go into the development of new digital high performance platform. The required amplitude and phase stability has not been reached for the injector area yet (factor 2-10). This means, developments have to be done to achieve this goal. What is the consequence in putting very much manpower in ATCA developments? Would this manpower be able to improve existing systems in such a way to fulfill the necessary field stability?
* What are the potential show stoppers in present (VME based) systems?
* Are the 2 x 3 weeks maintenance/shutdown/machine studies periods in 2008 enough in order to prepare a full ATCA system test by end of 2008?
* How is time stamping done across the machine? Global time stamping along the linac seems to be done only by the event system. The resolution of this was not clear.
* The expected data rates and required communication bandwidths were not really clear.
* Is there a scheme to synchronize the ADC clocks of different LLRF stations? Is this envisaged?
Additional
What are the evaluation critera for the proof-of-concept prototype? What facilities are required to perform evaluation, eg HLRF, beam (ie FLASH),…?
What is the back-up solution if ATCA is found not to be adequate?
Please provide a high level schedule and major milestones between now and XFEL commissioning
What is the maximum power consumption of the fully-loaded carrier card?
What is the maximum data rate anywhere in the system?
What is the backup if any of the AMC module designs are unsuccesful?
What is the backup if RocketIO is inadequate, eg to to meet latency requirements?
What is the backup if any given contributor does not have capabilities to develop cicuits with Xilinx FPGAs, eg they use Altera intead?