## Slide 1: Rack cooling issues
23.10.2012

## Slide 2: Rack cooling issues
1. Water pumps are already installed: too late to change them
Estimated cost associated with changing water pumps: 150,000 EUR
2. Pipes are already on site, ready to be assembled: too late to modify the water flow distribution (using bigger pipes etc...)
3. Going back from 20 deg.C to 18 deg.C costs a lot of money. Until now, no clear case was made that the cost of early aging electronics is higher than the cost of lowering the incoming water temperature.
Cost of aging electronics is unclear (no experience, MTCA system is a new technology)
4. WP02 needs to come up with a more accurate estimate of their total heat load. Is it really 5.5kW per rack, with what accuracy ?
MTCA: 1200W
PSM: 200-300W
LOGM: 100W
PZ16M: 100W
DCM: 100W
----------------
LLRF : 1700-1800W
2x LLRF : 3600W
+ 500W from fans and infrastructure
QUESTION: other users in same racks/shelves ?

## Slide 3: Rack cooling issues
5. There are capacitors on the market with better heat characteristics. Even off-the-shelf electronics can have these capacitors replaced with better ones. What is the cost associated with this ?
A board typically has 50-100 Tantalium Elkos capacitors, which are the most temperature critical.
The number of other capacitors is around 100-300 and these are also critical capacitors.
One can find substitute parts from the automotive industry, but in a different form factor, which means a board redesign (1 iteration > 4-6 months) and it is unclear if we are not limited by space (larger form factor might be a problem). Cost associated with new board iteration: ~50 k EUR (15 k for hardware, 35 k for personnel ~5 months for summing up all FTE)
Replacing capacitors on commercial boards:
half-reassembly using machine is not possible  has to be new assembly (means new production)
for our boards, care is already taken to use better specs C (for heat)
6. It appears WP02 is only looking at one end of the problem, by proposing a change on the external cooling, rather than looking at internal options to make the electronics more robust to heat stress.
Replace critical capacitors on LLRF designed boards  PLANNED !
Improve crate air flow, feedback to vendors  DONE ! (8U  9U ELMA crate redesign)
Use of local heat sinks for crucial parts (FPGA, CPU)
One option would be to design custom made heat sinks for individual boards (the whole board)
a. cost 300-500 EUR / board (x 1000 boards). As an example, in-house production (ZM) for a top and bottom housing cost 1250 EUR
b. associated risk with heat sinks is changing high frequency behavior of the board (unclear)

## Slide 4: Rack cooling issues
7. What does it mean, a capacitor has a lifetime of 2.7 years. Is it creating a short or is its capacitance simply lowered ? How many capacitors are we talking about ? Which component does this affect ? What does it mean for the system when a capacitor is dead ?
a. capacitance lowers (outside tolerance)  affects DC/DC converters voltage  board behavior is unpredictable
b. capacity becomes short  this is a clear board malfunction
9. Can you prove that if the water is cooled down by 2 degrees, the airflow will decrease by 2 degrees ?
We’ve observed that with the current inlet air temperature, the crate temperature management is maxed-out (fans 100% all the time, no margin, already saturating regulation ability)
This is clear violation of the crate cooling specifications (cf Industrial Partner email at end)
Other points:
Community general agrees on 21 deg. C inlet air temperature for high computing systems (industry and research)  reference from industry vendors
Most of the integrated circuits do not give a Mean Time Between Failure (MTBF) number. The assumption that military versions with operating temperatures of 125 deg.C instead of 85 deg.C have a better MTBF was refuted (same life time, only more thoroughly tested and usually sturdier packaging).
Furthermore, a lot of chips are not available in military versions. When available, the price for a military version is 3-10x higher than the standard one.