## Slide 1: Rack Impedance: Calculations, Measurements, Conclusions
H. Kapitza (FLA)
LLRF Rack Meeting
16. Nov. 2012
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: Outline
What is a rack?
Metal sheet impedance
Sheet resistance calculation
Measurements
Conclusions

## Slide 3: What Is A Rack?
A rack is essentially an assembly of multiply bent metal sheets, held together by screws and/or welds.
Besides storing crates mechanically, a rack also serves electrical purposes:
  The metal cabinet is a shield against external electromagnetic fields. Rack manufacturers provide diagrams of the frequency-dependent shielding effectiveness (Schirmdämpfung) of their products.
  The rack metal is part of the hierarchical grounding system in a large facility like XFEL. As such it is part of a low impedance bypass for common mode noise currents.

## Slide 4: Metal Sheet Impedance
Impedance:
and of metal sheets are orders of magnitude lower than for metal wires, because currents in a sheet always have the freedom to flow along the path of least impedance. A simple DC resistance measurement will already characterize the metal sheet quality.

## Slide 5: Sheet Resistance Calculation
For the parameters
resistivity
sheet thickness
measuring distance
contact radius
the resistance is
(steel) = (Cu) = 170 nΩm
= 1 mm, = 2 m, = 5 mm yields = 0.324 mΩ.
Due to the logarithm the dependence on is quite weak.

## Slide 6: Loop Impedance Measurement
Using a booster cable, make the rack part of a closed current loop. Measure Z(loop) and subtract Z(cable) to obtain Z(rack).

## Slide 7: Loop Impedance Measurement
A lot of contact resistance in the cable clamps. Bad reproducibility of contacts. Lowest measurement range 25 – 250 mΩ. ►►► Forget about this method.

## Slide 8: Rack Resistance Measurement
Isabellenhütte IMR-B-R020 USB-Mikro-Ohm-Meter with Kelvin probes for true 4-point resistance measurements:
Device at work in tübbing factory
Kelvin probe
USB

## Slide 9: Rack Resistance Measurements
0.092 mΩ
4.8 mΩ
Measurements on an old rack:
R = 0.092 mΩ for a distance of about 50 cm is in good agreement with the calculation of R = 0.324 mΩ for a distance of 2 m.
Each screw adds a contact resistance of 2.8 mΩ.
Next I measured on two of the new Schroff racks.

## Slide 10: Rack Resistance Measurements
0.042 mΩ
0.048 mΩ
7 mΩ
3 mΩ
top plug
SMD conn.
leftmost rack (seen from the back)

## Slide 11: Rack Resistance Measurements
3.6 mΩ
1.6 mΩ
2.0 mΩ
0.046 mΩ
plug plate
rightmost rack (seen from the back)

## Slide 12: Conclusions
A perfect rack (without screws) made of 1 mm thick steel sheet would have a resistance R ≈ 0.5 mΩ from top to bottom.
Screw joints add largely varying contact resistances of a few mΩ. This makes it difficult to specify a target value defining rack quality.
Assume good contact at the screw joint only, not between screws. Hence set screws well and often. A grid is as good as a plane if the mesh size is much smaller than the wavelength: This means f < 30 MHz for d = 20 cm. There must be no paint or other insulators in contact areas, absolutely not at the screws!
Further improvement comes from rack placement on a ground plane, but that’s not important here.