## Slide 1: Commissioning of XFEL Cryogenic Installation
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: Overview
The HERA refrigeration plant
Overview of XFEL cryogenic equipment
Commissioning of XFEL cryogenic equipment
Summary
Requirements on XFEL refrigerating plant
Warm pumps vs. cold compressors
HERA refrigerating plant XFEL refrigerating plant
Notes: Before you start editing the slides of your talk change to the Master Slide view:
Menu button “View” > Slide Master:
Edit the following items:
1. On the Title slide (second master slide)
a) Click to add title of your talk
b) Click to add subtitle (conference, location, name of the speaker, date)
2. On the Slide Master (first master slide)
a) The 1st row in the violet header: Delete the existent text and write the title of your talk into this text field b) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area.
Close Master View

## Slide 3: The HERA Refrigerating Plant

## Slide 4: The (former) HERA Refrigerating Plant
LP-Compressors
HP-Compressor
Purify-Units
Cryogenic
Purifier
Cold Box
Distribution Box
Consumer

## Slide 5: The (former) HERA Refrigerating Plant
Redundancy:
Distribution Box
Coldbox
Compressors
Dewars
HERA North
HERA South
FLASH, CMTB, MTH …
(1)
(2)
(3)

## Slide 6: Requirements on XFEL Refrigerating Plant
100 cryomodules, 10 Hz, Qo=10**10, 23.6 MV/m
Requirements on XFEL refrigerating plant (17.5 GeV)
1 injector, 3.9 GHz cryomodule
2K: 1869 W
5/8K: 3593 W
40/80K: 23923 W
Operation: 24 h/d, 7 d/week
Run periods of 2-3 years without scheduled break
Refrigerator availability > 99%

## Slide 7: Requirements on XFEL Refrigerating Plant
  Study was conducted 2006
Industrial Study Linde Kryotechnik and its Results:
Based on TDR XFEL refrigerator requirements
Subject: re-use of HERA refrigerator for XFEL
Process investigation including CC operation (cold compressors)

## Slide 8: Requirements on XFEL Refrigerating Plant
8
  2 HERA refrigerators (subplants) + 2K system (cold compressors) could be modified to XFEL-refrigerator
Industrial Study Linde Kryotechnik and its Results:
Advantages:
Only ½ of investment costs compared to new refrigerator (fixed price for 2006)
No extra civil engineering effort
Utilities exist
Disadvantages:
Lower efficiency compared to new plant
Re-use of worn equipment
Parallel operation of 2 cold boxes challenging (symmetrical operation)
Use of existing HERA helium refrigerator = cheapest solution (decreasing investment costs for the XFEL refrigerator about factor 2) reason to realize this solution

## Slide 9: 2K Operation – Warm Pumps vs. Cold Compressors
→ 2K return gas cannot be used for cooling process in coldbox (precooling of high pressure warm gas flow)
Cold He-vapour needs to be warmed up before entering the warm He-pump (heat-exchanger and/or ambient air)
Refrigerating plant / Cooling process
(Warm) He – pump
30 mbar = 2K
2 phase pipe
2K gas return pipe

## Slide 10: 2K operation – Warm Pumps vs. Cold Compressors
Some facts about cold compressors (in contrast to warm He-pumps)
Small dynamic range
Sensitive towards massflow-, pressure-, temperature changes
Each system is unique
(Re-)start of cold compressors is time intensive
DESY has no operational experience with cold compressors

## Slide 11: 2K operation – Warm Pumps vs. Cold Compressors
Why using sensitive cold compressors instead of robust warm He-pumps?
Cold compressors
Investment costs:
Energy consumption:
Warm pumps
Operating costs/year:
x
35 KW
42000 EUR
x + 2 Mio EUR
1650 KW
1.98 Mio EUR
( 4K → 2K)
(8000 h/year, 0.15 EUR/KWh)
~ 2.5 Mio EUR more energy costs for warm He-pumps (per year)
(4K → 2K)
+ 1.39 Mio EUR
(liquefaction costs)
+ 871000 EUR
(re-cooling costs)
3.37 Mio EUR
0.9 Mio EUR
Two reasons for the use of cold compressors:
2. Plant efficiency
1. Operational costs

## Slide 12: Warm pumps vs. cold compressors
Start-up: 17.5 GeV version
Spec:
2K: 1896 W
5K: 3593 W
40K: 23923 W
DESY specification for XFEL refrigerating plant
Operating 17.5 GeV Linac with one refrigerator (subplant) would save > 500.000 EUR primary energy costs (only possible with cold compressors)
Two reasons for the use of cold compressors:
2. Plant efficiency
1. Operational costs
Offer (one coldbox):
2K: 2010 W
5K: 3030 W
40K: 20175 W

## Slide 13: HERA refrigerating plant -> XFEL refrigerating plant
Redundancy:
Distribution Box
Coldbox
Compressors
Dewars
HERA North
HERA South
FLASH, CMTB, MTH …
(1)
(2)
(3)
Filters
LTP
LTP: Low Temp. Purifier
XFEL

## Slide 14: HERA refrigerating plant -> XFEL refrigerating plant
(FLASH-) Redundancy
Distribution Box
Coldbox
Compressors
Dewar
XFEL
Cold Compressor Box
Warm Compressors
Overhauling
Commissioning of both XFEL subplants is finished.

## Slide 15: HERA refrigerating plant -> XFEL refrigerating plant
(FLASH-) Redundancy
Distribution Box
Coldbox
Compressors
Dewar
DB54
The XFEL refrigerating plant:
Commissioning of both XFEL subplants together with DB54 is finished, but operation parameters are still being optimized.

## Slide 16: Overview of XFEL Cryogenic Equipment
AMTF
CMS = Cryomodule string
EC = End Cap
Main Linac
CM
Distribution Box
XLVB
Distribution Box
XIVB
FB
FB
CM
FC
EC
3,9 GHz
FC
EC
3,9 GHz
Injectors
Building 54
Shaft & Tunnel
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
SCB = String connection box
XLTL1
XLTL3
XLTL2
CMS
FC
EC
CMS
FC
EC
CMS
SCB
EC
CMS
FC
SCB
Warm
He-Pumps
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
FC = Feed Cap
Bunch Compressor Bypass Transferline
Feed Cap
each cryomodule consists of:
8 1.3 GHz 9-cell Nb cavities (2K)
1 magnet package (2K)
2 thermal shields (5-8K;40-80K)
8 main RF couplers
8 cold tuners
XFEL requirement: 23.6 MV/m
Cryomodule cross-section
2.2 K forward
40 K forward
2 K 2-phase
cavity
2 K return
80 K return
8 K return
RF main coupler
magnet current feedthrough
5 K forward
4 K shield
70 K shield
End Cap
string connection box

## Slide 17: Commissioning of XFEL Cryogenic Equipment
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
Building 54
Commissioning of cryo equipment in building 54 is almost finished

## Slide 18: Commissioning of XFEL Cryogenic Equipment
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
Building 54
Problem: Transferline XRTL is delayed (~1 year)
Cold compressor box CB44 cannot be commissioned ‚in time‘
Time loss is not acceptable
CB44 is temporarily installed in building 54 with ‚commissioning transferline CXRTL‘
Commissioning of Cold Compressor Box (CB44)

## Slide 19
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
Building 54
CXRTL
Commissioning of XFEL Cryogenic Equipment
Pre-commissioning of XFEL refrigerator with CB44 in building 54
Now – September 2014
Partial compensation of delayed XRTL

## Slide 20
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
Building 54
CXRTL
Transport of CB44 from building 54 to final location of installation in XSE
Commissioning of XFEL Cryogenic Equipment
September 2014
Time can be used for further tests (symmetrical operation of both subplants)

## Slide 21
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
Contributions:
LINDEKRYOTECHNIK
BINP
DEMACO
Building 54
Commissioning of XFEL Cryogenic Equipment
November 2014
Installation of transferline XRTL
November 2014 – December 2014
Final commissioning of XFEL refrigerator with CB44 in XSE

## Slide 22
CM
Distribution Box
XLVB
Distribution Box
XIVB
FB
FB
CM
FC
EC
3,9 GHz
FC
EC
3,9 GHz
Injectors
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
Warm
He-Pumps
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
Commissioning of XFEL Cryogenic Equipment
January 2015 – February 2015
Commissioning of cryo equipment of injector
First cool-down of injector
March 2015

## Slide 23
CM
Distribution Box
XLVB
Distribution Box
XIVB
FB
FB
CM
FC
EC
3,9 GHz
FC
EC
3,9 GHz
Injectors
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
XLTL1
XLTL3
XLTL2
CMS
FC
EC
CMS
FC
EC
CMS
SCB
EC
CMS
FC
SCB
Warm
He-Pumps
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
Commissioning of XFEL Cryogenic Equipment
– June 2016
Installation of cryogenic equipment in tunnel
  XLTL1-3, FCs, CMSs, Ecs, SCBs

## Slide 24
CM
Distribution Box
XLVB
Distribution Box
XIVB
FB
FB
CM
FC
EC
3,9 GHz
FC
EC
3,9 GHz
Injectors
XFEL
Refrigerator
Distribution Box
DB54
CC Box
CB44
SC
SC
SC
SC
CB 41
SC
SC
SC
CB 43
SC
XRTL
XLTL1
XLTL3
XLTL2
CMS
FC
EC
CMS
FC
EC
CMS
SCB
EC
CMS
FC
SCB
Warm
He-Pumps
Contributions:
LINDE KRYOTECHNIK
BINP
DEMACO
June 2016
Commissioning of XFEL Cryogenic Equipment
First cool-down of XFEL-Linac

## Slide 25: Commissioning of XFEL Cryogenic Equipment
Why is the commissioning of the cryogenic equipment that time consuming?
Coldbox
Operation of ‚new machines‘ like cold compressors
Just some examples:
Complexity of cryogenic system
Leak tests
Damaged components (e.g. turbines)

## Slide 26: Commissioning of XFEL Cryogenic Equipment
Why is the commissioning of the crygenic equipment that time consuming?
Operation of ‚new machines‘ like cold compressors
Just some examples:
Complexity of cryogenic system
Leak tests
671 control valves
2647 temperature sensors
800 pressure sensors
212 flow sensors
207 level sensors
433 regulation loops
> 22000 records (description of process parameters)
> 220000 properties (set values, critical values, scanrates, calculation codes, etc.)
Damaged components (e.g. turbines)

## Slide 27: Summary
27
The HERA cryo plant is modified and upgraded with a cold compressor system (→ XFEL cryo plant) to operate XFEL
Commissioning of complete cryo installation is time consuming
Operation of ‚new components‘ (cold compressors)
Complexity of cryogenic system (e.g. number of properties to be defined, calculated, checked, etc.)
Dependency on delivery of ‚critical components‘ (e.g. XRTL)
Target time for first cool-down of
Injector: March 2015
XFEL-Linac: June 2016