## Slide 1
Capacitive Energy Storage for the PS Booster Accelerator
Fulvio Boattini
CERN Technology Department | Electrical Power Converters
Acknoweledgements: Charles-Mathieu Genton, Stefano Rocca, Andres Marquez

## Slide 2: The CERN PS Booster accelerator

## Slide 3
PS Booster accelerator: facts & figures

## Slide 4
PS Booster ring was developed in the 60’s (first p+ in 72) to increase injection energy in the PS from 50 to 800 MeV as required by the ever increasing beam intensities.
Since its creation, the PS Booster extraction energy has already been increased twice:
800MeV to 1GeV (1988)
1 GeV to 1.4GeV (1999)
Pag 4
PS Booster accelerator: facts & figures
4

## Slide 5
dipole
quadrupole
4 magnets into one structure
External rings need more current
Trim converter required
Ltot=0.18H
Rtot=0.5ohm
TOTAL MAGNETS IMPEDENCE
4 rings 157m circumference accelerator. 32 dipoles and 48 quadrupole magnets connected in series.
Takes particles from Linac2 at 50MeV and accelerates them up to 1.4GeV
Pulsed operation:1.2s cycles repeated continuously 300days/year 24h/day
PS Booster accelerator: facts & figures
5

## Slide 6
From 1.4GeV to 2GeV
Increase of energy is limited by Magnet max and rms current.
(*) Chamonix 2010
30% more peak current
10% higher r.m.s. current for magnets cooling limitations
40% Higher voltage and 30% higher current from power converter
PS Booster accelerator: facts & figures
6
Reduces the negative effects of space charge on beam allowing higher beam intensity.

## Slide 7
PSB 1.4 GeV:
all magnets connected in series
PSB 2 GeV:
Rings 1&4 + QFO
Rings 2&3 + QDE
PS Booster accelerator: facts & figures
New circuit connection

## Slide 8
2GeV increase is compatible with the 10% maximum increase in rms current
Irms 1.2s =2250A
Magnet current
Magnet voltage
Magnet current
Magnet voltage
Irms0.9s=2450A
2GeV cycle will be 1.2s duration 5.25kApk 2x2.5kVpk
Irms is 2450Arms
1.4GeV cycle is 1.2s duration 4kApk 3.6kVpk for 1.4GeV
Irms is 2250Arms
PS Booster accelerator: facts & figures

## Slide 9
POPS-B MPC (main power converter)
9

## Slide 10
The project includes the following working units:
The total budget is 16MCHF
Building + services: 3.4MCHF
MPS high power converters: 12 MCHF
Trims: 0.6MCHF
Commissioning 2019-20 (LS2)
Construction of a new building to host the new MPS
Realization of the POPS-B high power converters (2+1 units)
Realization of the quadrupole trims (+ injector and extraction trims)
The total LIU PSB budget is 21.7MCHF + 3MCHF for LIU-L2B
10
POPS-B MPC : main project numbers
Power for PS-Booster

## Slide 11
POPS-B MPC : present realization
4X12 pulse thyristor bridges directly connected to the AC network via a 3 winding 18kV/389V transformer
13 MW peak active power
15 Mvar peak reactive

## Slide 12
A storage capacitor bank connected on the DC side provide power decoupling from the network.
The storage capacitance is around 0.3F (@5kV Udc nominal)
UDC
Vout
Imag
Vac
Power transformer:
Power=2.5MW
Vac=2000Vrms
Storage Capacitors:
Cap=0.3F
Vmax=5000V
Vmin=3000V
Load (Mag):
Lmag=100mH
Rmag=250mOhm
Output:
Imag_pk=6000A
Imag_rms=3000A
Vout_pk=3000V
Additional common mode filter inductance required for DVripple
POPS-B MPC: new topology
12

## Slide 13
Storage capacitors discharge
Instantaneous power to magnets
Instantaneous power from storage capacitors
Instantaneous power from AFEs
Storage capacitors operation
POPS-B MPC: storage capacitors
13

## Slide 14
POPS-B MPC: storage capacitors
Variable saturation limits on Udc control loop
14

## Slide 15
Reduced scale prototype:
1/10.000 on power
1/100 on currents and voltages
Rapid control prototyping
Storage capacitors
IGBT converters
POPS-B MPC: prototype tests
15

## Slide 16
The new building B245
16

## Slide 17
The new Building B245
17

## Slide 18
The new Building B245
18

## Slide 19
Storage Capacitors
19

## Slide 20
Storage capacitors: AC+DC voltage stress
20

## Slide 21
1100 mm
POPS capacitor bank at CERN.
6 Containers 65 tons
The two main solutions are NON-IMPREGNATED and OIL-IMPREGNATED polypropylene metalized film capacitors
Series-parallel connection
Storage capacitors: technology
21

## Slide 22
Series-parallel connection
Storage capacitors: technology
22

## Slide 23
Metallized PP film as new
Flash Over on surface between + and –
Excessive surface electro-erosion of the metallization
5mm
Flashover between polarities….
20mm
400mm
Extended corrosion of metallization along the surface
175 mm
Storage capacitors: ageing
23
Notes: This is how the double layer metallized polypropylene film looks like when it is brand new.
During the exploitation of the POPS power converter we faced several problems with capacitors.
Excessive surface electro-erosion
Huge metallization corrosion
Flash-over between polarities
The capacitors seems to age faster than foreseen on the field. The common cause seems to be the alternating voltage component.
With 65 tons of installed capacitors and another 50 tons to be purchased in the near future for a new project, we decided that an investigation of the characteristics of these capacitors was worth the effort and started the design of a testing circuit for capacitors.

## Slide 24
Storage capacitors: accelerated ageing tests
4850 V
3300 V pk to pk
failed
Preliminary results on six different solutions. Tested 900h on a single unit/solution
CERN capacitor accelerated test laboratory
Max Cut = 2000 uF
Max Vdc = 5500 V
Max Vac = 3000 V
Max freq = 8 Hz
Max temp = 70ºC
24

## Slide 25
Picture of the interior
Reduced scale samples
Full scale unit
Thermal Chamber
AC source;
DC source;
Control crate;
Power cabinets
Thermal chamber;
Reduced scale capacitors under test;
Full scale capacitor under test.
1
5
6
7
2
3
4
Storage capacitors: accelerated ageing tests
Capacitors accelerated ageing lab
25

## Slide 26
Inspection of the film conditions
Electro-corrosion appears on the metallization: aluminum oxide Al2O3
On all Solutions from three to six
More evident on the external film layers
600 µm
Storage capacitors: accelerated ageing tests
2500 Vs 3300 Vac pk2pk Non Impregnated
2500 Vs 3300 Vac pk2pk Impregnated
1.27
2.33
26

## Slide 27
POPS: POwer for PS
First example at CERN using capacitors for storing energy. In operation since 2011.
POPS-B: POwer for PS Booster
New MPS for the PS-Booster, LIU project.
Installation in LS2.
Sirius power converter
46 “s” type bricks TT2 (LS2)
40 “s” type bricks PSB (LS2)
125 “s” type bricks East Area (under discussion)
65 Tons of 5 kV capacitors Estimated cost ≈ 2.5 MCHF
52 Tons of 5 kV capacitors Estimated cost ≈ 2 MCHF
16 Tons of 0.4 kV capacitors Estimated cost ≈ 1 MCHF
Storage capacitors: application at CERN
27

## Slide 28: Conclusions
The new PSB main power converter will include an energy storage mean in form of a capacitor bank;
Energy storage for pulsed applications efficiently smooth the interface of the power converter with the electrical network;
No need of an SVC for compensating the reactive power;
Storage capacitor technology is mature for this application
  …. but carefully consider the presence of the AC component !

## Slide 29
Thank you for your attention

## Slide 30
Increasing beam energy will decrease the factor: leading to higher intensity with same maximum |Q| (a value around 0.3 seems to be accepted as limit).
The main limitation to machine performance appears to be connected with tune shift due to space charge.
Linac4 will increase PS Booster injection energy from 50 to 160MeV (factor of 2 in and in p+ density).
(*) Chamonix 2010
Pag 7
From 1.4GeV to 2GeV: the rationale
30

## Slide 31
The improved performance related to Linac4 can only be exploited only lifting the space charge limit in the PS.
This is achieved by increasing the injection energy in the PS.
Mainly for Magnet limitations (max current), it is not possible to recover the same factor of 2 given by the Linac4.
With 30% magnetic field increase (10% Irms increase) a factor 1.6 can be achieved.
(*) Chamonix 2010
POPS-B 29 January 2015
Pag 8
From 1.4GeV to 2GeV: the rationale
31

## Slide 32
The improved performance related to Linac4 (50 to 160 MeV @ PSB injection) can be fully exploited only by lifting the space charge limit in the PS.
This is achieved by increasing the injection energy in the PS.
Increase of energy is limited by Magnet max and rms current.
(*) Chamonix 2010
POPS-B 29 January 2015
Pag 8
30% more peak current
10% higher r.m.s. current for magnets cooling limitations
Higher voltage and current from power converter
PS Booster accelerator: facts & figures
32

## Slide 33
4X12 pulse thyristor bridges directly connected to the AC network via a 3 winding 18kV/389V transformer
Performance limited to 3.6kV x 4kA peak power on the magnets.
Reactive power (and Active peak power) drawn from the 18kV network already at limit.
Rms current in transformers already close to the limits.
Present MPS limitations

## Slide 34
Due to Udc voltage limitation, 2GeV cycle would be too slow. To high rms for converters and for magnets
Present MPS limitations
Irms1.2s=2250A
Irms1.2s=3000A
Irms0.9s=2450A
18kV network quality at risk due to further increase in power peak

## Slide 35
P+ energy increased from 1.4 to 2GeV. Current increased from 4 to 5.5kA
Magnets will be split into 2 equivalent series
2 separated power converters will be used to power each half string of magnets
Only 2 trim converters required for quadrupoles
L=0.09H
R=0.25ohm
L=0.09H
R=0.25ohm
Magnet current
Magnet voltage
Future cycle will be 0.9s duration 5.5kApk 2x2.5kVpk for 2GeV
Irms on cycle duration is 2450Arms
2GeV cycle developed by physicists
Booster 2GeV MPS: general introduction